## Slide 1: Knx Interworking

## Slide 2: Outline
Introduction
Definition
Topology
Communication
Knx Telegram
Datapoint Types
  Structure
  Datapoint Types Classes
  Samples

## Slide 3: Introduction
  multi-vendor interworking : products of different manufacturers
  cross-discipline interworking : products of different application fields
  standardization of the protocol
  rules for the useful data inside telegrams

## Slide 4: Introduction Cont.
  European Installation Bus Association (EIBA)
  formats for common functions
    switching
    dimming
    blinds control
    integer and float values
    Percentage
    date/time
    HVAC modes
  EIB Interworking Standards (EIS)

## Slide 5: Definition
Knx interworking : “The situation where products sending and receiving messages can properly understand signals and react on them without additional equipment” by knx.org
Advantages
  choose between products of a large number of KNX manufacturers
  single planning and configuration tool like ETS
  worldwide uniform training scheme
  facilitate the development of gateways between KNX and other systems (like DALI and BACnet)
  …

## Slide 6: Topology (line)
  exchange information by means of telegrams
  maximum of 64 bus devices
  requires an appropriate power supply
  The actual number of devices is dependent on the power supply selected and the power input of the individual devices

## Slide 7: Topology (area)
  up to 15 lines can be connected to a main line via a line coupler
  possible to have up to 64 bus devices on the main line
  Each line, including the main line, must have its own power supply unit

## Slide 8: Topology (several areas)
  maximum of 15 functional areas, more than 58,000 bus devices can be connected to the bus system

## Slide 9: Topology (maximum)

## Slide 10: Topology (coupling unit)
  coupling unit is provided with a filter table
  received group telegrams are routed if they are listed in the filter table
  each line works independently
  line repeater passes on all telegrams; it has no filter table

## Slide 11: Topology (routing counter)
  initial count value is 6
  Each coupler decrements the routing counter and passes on the telegram as long as the value is not 0

## Slide 12: Topology (group objects)
group address
  Actuators can listen to several group addresses
  Sensors can only send one group address per telegram
group objects are memory locations in bus devices
several group addresses can be assigned to one group object but only one is the sending group address

## Slide 13: Topology (group objects)
  If the upper left rocker is pressed for example, the two-fold switch sensor writes a “1” to its group object with the number 0. As the communication and transmit flag are set for this object, this device will send a telegram on the bus with the information “Group address 1/1/1, write value, 1”.
  All the bus devices throughout the KNX installation that also have the group address 1/1/1 will then write “1” in their own group object.
  In our example, the “1” is written in group object no. 0 of the actuator.
  The application software of the actuator establishes that the value in this group object has changed and executes the switching process.

## Slide 14: Topology (group object flags)
  “master switch” for communication
  if this flag is not set, the object cannot send or receive telegrams
  It is set for all objects by default
  If this object is linked to a group, an acknowledgement is sent even though the communication flag has been deleted

## Slide 15: Topology (group object flags)
  enables the object value to be read
  response telegram is only sent after a read telegram if the read flag of the object has been set
  set by default for status objects

## Slide 16: Topology (group object flags)
  enables the object status to be modified via the bus on the basis of a telegram
  set by default for all switch objects, value objects (actuator) as well as all push button objects

## Slide 17: Topology (group object flags)
  enables the group object to send telegrams
  sending of telegrams can be triggered e.g. by a push button action, a variation in the temperature or a change in the object status
  set for sensors by default

## Slide 18: Topology (group object flags)
  If the update flag is set, a response telegram of a read procedure is interpreted as a write telegram

## Slide 19: Topology (group object flags)
  If the Read on Init flag is set, the bus device will independently read the value of its sending group address at initialisation

## Slide 20: Communication
Connection-oriented Communication
  point-to-point [P2P] connection
  highly secure, but is not very bandwidth effective
  the Transport Layer as well as the Link Layer will generate messages confirming reception of data
  rejected telegrams are repeated up to three times
  Ex. talking to one single person and checking after each question, whether he/she understood the question
  In KNX : Downloading group addresses, parameters and/or application program from the PC (= ETS) into the KNX device

## Slide 21: Communication
Connectionless Communication
  the address must be sent together with the useful data after each data request
  no confirmation of the data received
  the device sending the information does not guarantee the correct order of the transmitted data blocks
  one single message it is possible to reach all devices included in the installation
  only one common acknowledgement of receipt is received

## Slide 22: Communication
Connectionless Communication Cont.
  not be ensured that all devices have correctly received the sent message
  Ex. o talking to a group of persons and continuing with the next question if at least one person confirms that he/she understood the message
  In KNX :
    Normal operating mode of the KNX (telegrams with group addresses, Multicast, one to many communication)
    Broadcast (one to all communication)

## Slide 23: Knx Telegram

## Slide 24: Knx Telegram
  D5 : repeated telegram = 0, not = 1

## Slide 25: Knx Telegram

## Slide 26: Knx Telegram
  N_PDU last bit => D7 : group = 1, individual = 0

## Slide 27: Knx Telegram
  First bit : group = 1, individual = 0
  Following 3 bits : the value of the routing counter, which will play a role in the routing of the telegram across line and backbone couplers
  Following 4 bits : the length of the actual useful information in the telegram(depending on datapoint type)

## Slide 28: Knx Telegram
  First two bits :
  Following 4 bits : the sequence number(the communication type numbered)

## Slide 29: Knx Telegram
  First two bits :
  00 = a transport layer point to point connection is opened from the indicated sender to the indicated receiver
  01 = an existing transport layer point to point connection between the indicated sender and the indicated receiver is terminated/broken down

## Slide 30: Knx Telegram
  First two bits :
  10 = the transport layer of the indicated sender positively confirms to the indicated receiver reception of a previously received telegram.
  11 = the transport layer of the indicated sender negatively confirms to the indicated receiver reception of a previously received telegram.

## Slide 31: Knx Telegram
  First four bits : APCI

## Slide 32: Knx Telegram

## Slide 33: Datapoint Types
Structure

## Slide 34: Datapoint Types
Classes
  Simple Types : boolean values, pure numerical values
  Enumerated Types : limited number of values, no precise hierarchical order
  Structured Types : several parts which are combined in a datapoint
  “Multi-state” Types : encodable values follow a hierarchical sequence and all encodable values are meaningful (0-255)
  Status Types : report its operating mode to other devices, to be switched to a specific operating mode

## Slide 35: Datapoint Types
Formats

## Slide 36: Datapoint Types

## Slide 37: Datapoint Types

## Slide 38: Datapoint Types

## Slide 39: Datapoint Types

## Slide 40: Datapoint Types

## Slide 41: Datapoint Types

## Slide 42: Thanks